Typical Specifications for Acme UNISET Gas Detection & Control Unit

Parking Garages ( Maintenance Garages ( Fire Stations ( Loading Docks ( Ambulance Bays Suitable for small applications where the ventilation system will be hooked up directly to the Acme Uniset Gas Monitor.

- Supply, install and connect at locations shown on plans ACME UNISET Gas Detection and Control unit.  The UNISET will consist of one integral sensor or one remote sensor for any one of the following gases: CO, NO2, O2 and combustibles.

2. 	CO, NO2 and O2 sensors shall be electrochemical whereas the combustible sensors shall be catalytic bead (pellistors).  UNISET sensors shall be equipped with compensatory circuits for variations in relative humidity and temperature and maintain a high level of accuracy.  The UNISET unit will be capable of operating within relative humidity ranges of 15-90% and temperature ranges of 32oF to 104oF  (0oC to 40oC) with an optional capacity of operating at extended temperature ranges.

The unit is manufactured within an ISO 9001-2000 production environment.

The Uniset alarm levels are to activate fans, dampers and alarms and the unit is to be installed in accordance with the following parameters:

The CO operating levels shall typically be 35 PPM, 100PPM and 100PPM 30 minutes time-delayed (1-60min adjustable) for the LOW, HIGH and ALARM levels respectively.  NO2 operating levels shall typically be 1PPM, 2PPM and 3PPM for LOW, HIGH and ALARM levels respectively. O2 operating levels shall typically be <19.5%, <18% and <17% for LOW, HIGH AND ALARM levels respectively.   Combustible Gas operating levels shall typically be 20%, 30% and 40% L.E.L. for LOW, HIGH and ALARM levels respectively.  The UNISET shall have typically three SPDT relay contacts to operate at the selected operating levels, visual indicators and an alarm buzzer. The operating levels can also be programmed to have different time delays.

| Table of factory default operating levels | FIRST ALARM SET POINT (LOW) | SECOND ALARM SET POINT (HIGH) | THIRD ALARM SET POINT (ALARM) | RADIUS OF COVERAGE |
| --- | --- | --- | --- | --- |
| Carbon Monoxide (CO) | 35 PPM | 100 PPM | 100PPM 30Min | 50 feet |
| Diesel (NO2) | 1 PPM | 2 PPM | 3PPM | 50 feet |
| Combustibles | 20% L.E.L. | 30% L.E.L. | 40% LEL | 25 feet |
| Oxygen Deficiency (O2) | <19.5% | <18% | <17% | 20 feet |

- Sensing element shall require no more than a yearly calibration.  CO, NO2 and O2 sensors shall have a maximum life of 2 years whereas combustible gas sensors shall have a maximum life of 3 years.

- The UNISET shall be housed in a NEMA 3 robust PVC enclosure. Explosion-proof enclosure is also available.

- The remote sensor to control unit field wiring shall be done by using 2 x #18 (for CO/NO2/O2) or

4 x # 18 (for combustible gas) low voltage wires.